## RTD
SPARES FOR PR | [7 empty] | CHECKLIST | [5 empty] | Spare to be indent
SL.NO | INSTRUMENT | Qty Instld | Qty Req | TAG NO | DESCRIPTION | INSTALATION SITE | AVAILABLE | JUL | AUG | SEP | OCT | NOV | DEC | Qty
1 | PCI_THERMOCOUPLE | 1 | 1 | TE202 | 0 - 1200℃ graduation No. S, ø20 corundum ferrule-type flange matched with one nos. of flange with the same model, length 1200mm, explsion-proof type | HGG inside temp | 1 | 1 | 1 | 1 | 1
2 | PCI_RTD-PT100 | 2 | 1 | TE201 | Graduation No. Pt100, 0 - 100℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 100mm, total length 300mm, wear-resistant & explosion-proof type | BFG Temp at HGG inlet | 2 | 2 | 2 | 2 | 2
|  |  |  | TE203 |  | CA Temp at HGG inlet
3 | PCI_RTD-PT100 | 4 | 1 | TE204 | Graduation No. Pt100, 0 - 600℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 300mm, total length 600mm, wear-resistant & explosion-proof type | Mill inlet Hot Gas Temp | 3 | 3 | 3 | 3 | 3
|  |  |  | TE319A | Graduation No. Pt100, 0 - 200℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 300mm, total length 600mm, wear-resistant & explosion-proof type | Mill outlet Gas Temp-1
|  |  |  | TE319B |  | Mill outlet Gas Temp-2
|  |  |  | TE320 |  | Bag filter inlet temp
4 | PCI_RTD-PT100 | 17 | 5 | TE205 | Graduation No. Pt100, 0 - 100℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 300mm, total length 500mm, wear-resistant & explosion-proof type | HGG inlet recirculation gas temperature | 6 | 6 | 6 | 6 | 6
|  |  |  | TE321 |  | Bag filter outlet temp
|  |  |  | TE330 |  | Chimney inside Temp
|  |  |  | TE331 |  | Bag filter hopper-1 temp
|  |  |  | TE332 |  | Bag filter hopper-2 temp
|  |  |  | TE333 |  | Fine coal Silo Temp-1
|  |  |  | TE336 |  | Fine coal Silo Temp-4
|  |  |  | TE337 |  | Fine coal Silo Temp-5
|  |  |  | TE338 |  | Fine coal Silo Temp-6
|  |  |  | TE501 |  | Top Temperature of injection vessel-A
|  |  |  | TE502 |  | BottomTemperature of injection vessel-A
|  |  |  | TE503 |  | Top Temperature of injection vessel-B
|  |  |  | TE504 |  | BottomTemperature of injection vessel-B
|  |  |  | TE505 |  | Top Temperature of injection vessel-C
|  |  |  | TE506 |  | BottomTemperature of injection vessel-C
|  |  |  | TE507 |  | Top Temperature of injection vessel-D
|  |  |  | TE508 |  | BottomTemperature of injection vessel-D
5 | PCI_RTD-PT100 | 1 | 1 | TE302 | Graduation No. Pt100, 0 - 100℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 300mm, total length 500mm, wear-resistant & explosion-proof type | Mill roller bearing Temp-1
|  |  |  | TE303 |  | Mill roller bearing Temp-2
|  |  |  | TE304 |  | Mill roller bearing Temp-3
6 | PCI_RTD-PT100 | 2 | 1 | TE334 | Graduation No. Pt100, 0 - 100℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 2000mm, total length 2200mm, wear-resistant & explosion-proof type | Fine coal Silo Temp-2 | 2 | 2 | 2 | 2 | 1
|  |  |  | TE335 |  | Fine coal Silo Temp-3
7 | PCI_RTD-PT100 | 2 | 1 | TE509 | Graduation No. Pt100, 0 - 100℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 0mm, total length 150mm, wear-resistant & explosion-proof type | MBF-B conveying line temp | 2 | 2 | 2 | 2 | 2
|  |  |  | TE510 |  | MBF-A conveying line temp
8 | PCI_RTD-PT100 | 2 | 1 | TE401 | Graduation No. Pt100, 0 - 100℃, ø16 armored 304 protecting tube, M27×2 matched base with fixed thread, insertion length 50mm, total length 150mm, wear-resistant & explosion-proof type | Nitrogen receiver Inlet temperature | 2 | 2 | 2 | 2 | 2
|  |  |  | TE402 |  | Compressure air receiver Inlet temperature

## LT
SL.NO | INSTRUMENT | Qty Instld | Qty Req | TAG NO | DESCRIPTION | INSTALATION SITE | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | Radar Model 5402ASH1E5YJAM1 | 3 | 1 | LE 101 | Model 5408A3SHA1E11R4AACAA4PC1M5Q4 Range:-0-14m, flange connection Suitable for medium:- coal | GH-1 Level | 1 | 1
2 |  |  |  | LE-301 |  | Raw coal storage silo level
3 |  |  |  | LE-302 |  | Fine Coal Silo
4 | PCI_level switch | 3 | 1 | LE-103 | Capacitance admittance level meter Armored 304 protecting tube ZG1", matched base with fixed thread, insertion length 200mm, total length 300mm, explosion-proof type Model:-L-2000D-SCA1-200NEX Suitable for medium:- coal Supply Voltage:- 24 VDC | Chute before Steep Aangl Conveyor Level | 0 | 0
|  |  |  | LE-104 |  | Chute before RCS Level
|  |  |  | LE-304 |  | Chute before VRM INLRT
5 | PCI UV Detector | 1 | 1 | XT203 | Model:-BWZJ-13T, Supply- 230VAC, Out Put- Switch Output. | HGG | 1 | 1
6 | PCI_Bed LVL Transmitter | 1 | 1 | LT-302 | Out Put- 4-20 mA, Range-= 0-50 mm, Supply 24V, Make- Autobolin | mill bed height | 1 | 1
0

## PT
SL.NO | SHORT DESCRIPTION | Qty Instld | SL.NO | Qty Req | TAG NO | DESCRIPTION | INSTALATION SITE | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_PT 3051CG4A +0-0.2Kg/cm² | 1 | 1 | 1 | PT-201 | Model No:- 3051CG4A52A1BH2S 1S00B915L 4M5J Range: 0 to 0.2Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation | BFG Pr at HGG inlet | 1 | 1
2 | PCI_PT 3051DR2A 0 -0.01-0.01Kg/cm² | 1 | 2 | 1 | PT-202 | Model No:- 3051DR2A52A1BH2S 1S00B915L 4M5J Range: -0.01 to 0.01Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation | HGG inside Pr | 0 | 0
3 | PCI_PT 3051CG3A +0-0.06Kg/cm² | 1 | 3 | 1 | PT-203 | Model No:- 3051CG3A52A1BH2S 1S00B915L 4M5J Range: 0 to 0.06Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation | CA Pr at HGG inlet | 0 | 0
4 | PCI_PT 3051CG3A -0.05-0Kg/cm² | 1 | 4 | 1 | PT-204 | Model No:- 3051CG3A52A1BH2S 1S00B915L 4M5J Range: -0.05 to 0Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation | Mill inlet Gas Pr | 0 | 0
5 | PCI_PT 3051CG4A -0.05-0.1Kg/cm² | 1 | 5 | 1 | PT-205 | Model No:- 3051CG4A52A1BH2S 1S00B915L 4M5J Range: -0.05 to 0.1Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation | HGG inlet recirculation gas pressure | 0 | 0
6 | Pressure transmitter |  | 6 |  | PT-206 | Range: --0.05-0.1Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation
7 | Pressure transmitter |  | 7 |  | PT-207 | Range: --0.05-0.1Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation
6 | PCI_PT 3051L5A-0.15-0Kg/cm² | 2 | 8 | 1 | PT-303 | 3051L5AG0QA-11BA01K5L5M3J1 Range: -0.15 to 0Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof typematched with one nos. of ø50 flange- | Mill outlet Gas Pr | 5 | 0
|  |  | 9 |  | PT-304 |  | Bag filter inlet pr | 0 | 0
7 | PCI_PT 3051DR2A -0.015-0Kg/cm² | 1 | 10 | 1 | PT-305 | Model No:- 3051DR2A52A1BH2S 1S00B915L 4M5J Range: -0.015 to 0Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation | Bag filter outlet pr | 0 | 0
8 | PCI_PT 3051L4A -0.15-0.15Kg/cm² | 1 | 11 | 1 | PT-306 | 3051L4AG0QA-11BA01K5L5M3J1 Range: -0.15 to 0.15Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof typematched with one nos. of ø50 flange | Fine coal Silo Pr | 0 | 0
9 | PCI_PT 3051CG7A -0.015-0Kg/cm² | 15 | 12 | 3 | PT-401 | Model No:- 3051CG7A52A1BH2S 1S00B915L 4M5J Range: 0-10Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof type, 304 ball valve direct installation | Nitrogen receiver Inlet pressure | 1 | 1
|  |  | 13 |  | PT-402
|  |  | 14 |  | PT-403
|  |  | 15 |  | PT-404
|  |  | 16 |  | PT-405
|  |  | 17 |  | PT-406
|  |  | 18 |  | PT-407
|  |  | 19 |  | PT-408
|  |  | 20 |  | PT-409
|  |  | 21 |  | PT-410
|  |  | 22 |  | PT-411
|  |  | 23 |  | PT-412
|  |  | 24 |  | PT-413
|  |  | 25 |  | PT-407 |  | Compressure air receiver Inlet pressure
|  |  | 26 |  | PT-502 |  | N2 Pr for injection vessel-A pressurisation
|  |  | 27 |  | PT-503 |  | N2 Pr for injection vessel-A fluidisation
|  |  | 28 |  | PT-504 |  | Conveying media Pr for injection vessel-A
|  |  | 29 |  | PT-506 |  | N2 Pr for injection vessel-B pressurisation
|  |  | 30 |  | PT-507 |  | N2 Pr for injection vessel-B fluidisation
|  |  | 31 |  | PT-508 |  | Conveying media Pr for injection vessel-B
|  |  | 32 |  | PT-510 |  | N2 Pr for injection vessel-C pressurisation
|  |  | 33 |  | PT-511 |  | N2 Pr for injection vessel-C fluidisation
|  |  | 34 |  | PT-512 |  | Conveying media Pr for injection vessel-C
|  |  | 35 |  | PT-514 |  | N2 Pr for injection vessel-D pressurisation
|  |  | 36 |  | PT-515 |  | N2 Pr for injection vessel-D fluidisation
|  |  | 37 |  | PT-516 |  | Conveying media Pr for injection vessel-D
|  |  | 38 |  | PT-601 |  | Cooling pump discharge water pr
10 | PCI_PT 3051L7A 0-10Kg/cm² | 8 | 39 | 2 | PT-501 | 3051L7AG0QA-11BA01K5L5M3J1 & STR74G-11A0000-000000000-0-AHC-11C-0-01A0-00-000 Range: 0-10Kg/cm², output signal: 4-20mADC, with digital display, HART digital communication, intrinsically safe & explosion-proof typematched with one nos. of ø50 flange (HONEYWELL) | Pressure of injection vessel-A | 4 | 4
|  |  | 40 |  | PT-505 |  | Pressure of injection vessel-B
|  |  | 41 |  | PT-509 |  | Pressure of injection vessel-C
|  |  | 42 |  | PT-513 |  | Pressure of injection vessel-D
|  |  | 43 |  | PT-517 |  | MBF-B conveying line pr
|  |  | 44 |  | PT-518 |  | MBF-B distributer inlet pr
|  |  | 45 |  | PT-519 |  | MBF-A conveying line pr
|  |  | 46 |  | PT-520 |  | MBF-A distributer inlet pr
TOTAL

## FT
SL.NO | SHORT DESCRIPTION | Qty Instld | Qty Req | TAG NO | DESCRIPTION | INSTALATION SITE | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_FT (0-2.5 kpa) | 1 | 1 | FT-201 | Model:-JSYH-BK-377+3051DP Range: 0-6000Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | BFG Flow at HGG inlet | 1 | 1
2 | PCI_FT (0-6 kpa) | 1 | 1 | FT-202 | Model:-JSYH-BK-325+3051DP Range: 0-6000Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | CA Flow at HGG inlet | 0 | 0
3 | PCI_FT (0-467.7 pa) | 1 | 1 | FT-203 | Model:-JSYH-YSG-820+3051DP Range: 0-30000Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | HGG inlet recirculation gas flow | 0 | 0
4 | PCI_FT (0-1427.8 pa) | 1 | 1 | FT-301 | Model No:-JSYH-YSG-920+3051DP Range: 0-65000Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Bag filter outlet gas flow | 0 | 0
5 | PCI_FT (0-16kpa) | 1 | 1 | FT-401 | Model No:-JSYH-BK-108+3051DP Range: 2500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Nitrogen receiver Inlet flow | 0 | 0
6 | PCI_FT (0-10kpa) | 1 | 1 | FT-402 | Model No:-JSYH-BK-108+3051DP Range: 2000Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Compressure air receiver Inlet flow | 0 | 0
7 | PCI_FT (0-7 kpa) | 4 | 1 | FT-502 | Model No:- JSYH-BK-48+3051DP Range: 300Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-A fluidisation | 0 | 0
|  |  |  | FT-505 | Model No:- JSYH-BK-48+3051DP Range: 300Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-B fluidisation | 0 | 0
|  |  |  | FT-508 | Model No:- JSYH-BK-48+3051DP Range: 300Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-C fluidisation | 0 | 0
|  |  |  | FT-511 | Model No:- JSYH-BK-48+3051DP Range: 300Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-D fluidisation | 0 | 0
8 | PCI_FT-(0-90 kpa) | 4 | 1 | FT-503 | Model NO:-JSYH-BK-32+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Conveying media Flow for injection vessel-A | 0 | 0
|  |  |  | FT-506 | Model No:- JSYH-BK-32+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Conveying media Flow for injection vessel-B | 0 | 0
|  |  |  | FT-509 | Model No:- JSYH-BK-32+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Conveying media Flow for injection vessel-C | 0 | 0
|  |  |  | FT-512 | Model No:- JSYH-BK-32+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Conveying media Flow for injection vessel-D | 0 | 0
9 | PCI_FT (0-20 kpa) | 4 | 1 | FT-501 | Model No:-JSYH-BK-48+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-A pressurisation | 0 | 0
|  |  |  | FT-504 | Model No:- JSYH-BK-48+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-B pressurisation | 0 | 0
|  |  |  | FT-507 | Model No:- JSYH-BK-48+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-C pressurisation | 0 | 0
|  |  |  | FT-510 | Model No:- JSYH-BK-48+3051DP Range: 500Nm³N/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | N2 Flow for injection vessel-D pressurisation | 0 | 0
10 | PCI_FT- (0-100 kpa) | 1 | 1 | FT-601 | Model No:- JSYH-BK-76+3051DP Range: 40m3/h. Output signal: 4-20mADC, with digital display, HART digital communication. See Throttle Device Consultation for others, matched with stainless steel tri-valve set | Cooling pump discharge water flow at return line | 0 | 0
TOTAL

## MCV
S NO | Short Description | TAG NO | Qty Instld | Qty Req | Specification | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_MCV DN300 | MCV-202 | 1 | 1 | Pg2.5kg/cm2;medium: normal air; control: 4～20mA,415VAC, explosion-proof Dia- DN300 Model-DN941-2.5C Make:- Gongkai | 0 | 0
2 | PCI_MCV DN400 | MCV-205 | 1 | 1 | Pg2.5kg/cm2; medium: hot gas, T≤200℃,control:4～20mA,415VAC, explosion-proof Dia- DN400 Model-DN941-2.5C Make:- Gongkai | 9 | 1
3 | PCI_MCV DN600 | MCV-203 | 1 | 1 | Pg2.5kg/cm2;medium: hot gas,T=400℃， control: 4～20mA , 415VAC,explosion-proof Dia- DN600 Model-DN941-2.5C Make:- Gongkai | 1 | 1
4 | PCI_MCV DN800 | MCV-206 | 1 | 1 | Pg2.5kg/cm2; medium: Hot gas,T≤100℃, control: 4～20mA,415VAC,explosion-proof Dia- DN800 Model-DN941-2.5C Make:- Gongkai | 0 | 0
5 | PCI_MCV DN300 | MCV-301 | 1 | 1 | Pg2.5kg/cm2; medium:hot gas,t＜100℃, control: 4～20mA, 415VAC, explosion-proof Dia- DN900 Model-DN941-2.5C Make:- Gongkai | 0 | 0
6 | PCI_MCV DN1000 | MCV-204 | 1 | 1 | Pg2.5kg/cm2; medium: hot gas, T=400℃, control: 4～20mA, 415VAC, explosion-proof Dia- DN 1000 Model-DN941-2.5C Make:- Gongkai | 0 | 0
7 | PCI_MCV DN350 | MCV-201 | 1 | 1 | ,Pg2.5kg/cm2; medium: coal gas,T＜100℃,control:4～20mA, 415VAC, explosion-proof Dia- DN350 Model-DN943-2.5C Make:- Gongkai | 0 | 0
8 | PCI_MCV DY1000 | MCV-302 | 1 | 1 | ,Pg2.5kg/cm2; medium: coal gas,T＜100℃,control:4～20mA, 415VAC, explosion-proof MODEL:-DY1000 MAKE -RIZHAO DEYI INTELLIGENT INSTRUMENT.CO.LTD | 0 | 0

## FSV&PCV
SNO | SHORT DESCRIPTION | TAG NO | Qty Instld | Qty Req | Item | Specification | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_FSV DN 350 | FSV-201 | 1 | 1 | Pneumatic quick cut off valves | Pg10kg/cm2; medium: fulverized coal, T＜100℃, DC24V, explosion-proof Model:- D643H-2.5C, DN 350,Size-185mm Make:- Gonkai | 0 | 0
2 | PCI_FSV DN 250 | FSV-506/513/520/527 | 4 | 1 | Pneumatic metal hard sealing butterfly valves | Pg10kg/cm2; medium: fulverized coal, T＜100℃, DC24V, explosion-proof Model:- D643Y-10C, DN 250,Size:-160mm Make:- Gonkai | 0 | 0
3 | PCI_FSV DN 25 | FSV-502/503/504/505 | 4 | 1 | Pneumatic explosion-proof ball valve | Pg2.5kg/cm2; medium: nitrogen,T＜100℃, DC24V,explosion-proof Model:- Q641-10C, DN 25,Size;187mm Make:- Gonkai | 4 | 4
4 | PCI_FSV DN25 SZ146 | FSV-511/518/525/532 | 4 | 1 | Pneumatic explosion-proof ball valve | Pg10kg/cm2; medium: nitrogen, T＜100℃, DC24V,explosion-proof Model:- Q641-10C, DN 25,Size:-146mm Make:- Gonkai | 0 | 0
5 | PCI_FSV DN40 | FSV-508/515/522/529/507/521/514/528 | 8 | 2 | Pneumatic explosion-proof ball valve | Pg10kg/cm2; medium: nitrogen,T＜100℃,DC24V, explosion-proof Model:- Q641-10C, DN 40,Size-177mm Make:- Gonkai | 6 | 6
6 | PCI_FSV DN50 | FSV-401/402/403 PSV-502 | 4 | 1 | Pneumatic explosion-proof ball valve | Pg10kg/cm2; medium: nitrogen, normal temp., control: switch value; DC24V,explosion-proof Model:- Q641-10C, DN 50,Size-198mm Make:- Gonkai | 1 | 1
7 | PCI_FSV DN100 | FSV-501 | 1 | 1 | Pneumatic explosion-proof ball valve | Pg2.5kg/cm2; medium: air with dust T＜100℃, control: switch value; DC24V,explosion-proof Model:- Q641-10C, DN 100,Size-277mm Make:- Gonkai | 0 | 0
8 | PCI_FSV DN 25 SZ180 | FSV-512/519/526/533 | 4 | 1 | Pneumatci explosion-proof three-way ball valves | Pg10kg/cm2; medium: nitrogen,T＜100℃,DC24V,explosion-proof Model:- Q645F-10C, DN 25,Size-180mm Make:- Gonkai | 3 | 3
9 | PCI_FSV DN250 | FSV-536/537/538/539 | 4 | 1 | Pneumatic dome valves | Pg10kg/cm2; medium: pulverized cial,T＜100℃， control: switch value; DC24V,explosion-proof Model:- YDF-10C, DN 250 Make:- Gonkai | 1 | 1
10 | PCI_PCV DN25 | PCV-503/507/511/515 FCV-501/502/503/504 | 8 | 2 | Film penumatic control valve | Pg10kg/cm2;medium: nitrogen,T＜100℃,DC24V,explosion-proof Model:- ZJHP-10C, DN 25,Size-187mm Make:- Gonkai | 0 | 0
11 | PCI_PCV DN40 FILM | PCV-504/508/512/516 | 4 | 1 | Film penumatic control valve | Pg10kg/cm2; medium: nitrogen,T＜100℃,DC24V,explosion-proof Model:- ZJHP-10C, DN 40,Size-222mm Make:- Gonkai | 0 | 0
12 | PCI_PCV DN40 | PCV-502/506/510/514 | 4 | 1 | Pneumatic explosion-proof control ball valve | Pg10kg/cm2; medium: nitrogen,T＜100℃,DC24V,explosion-proof Model:- VQ6T47H-10C, DN 40,Size-112mm Make:- Gonkai | 1 | 1
13 | PCI_PCV DN50 | FSV-509/510/516/517/523/ 524/530/531/534/535 | 10 | 2 | Pneumatic explosion-proof wearing-resistance ball valves | Pg10kg/cm2;medium: nitrogen,T＜100℃,DC24V,explosion-proof Model:- VQ647Y-10C, DN 50,Size-122mm Make:- Gonkai | 0 | 0
14 | PCI_PCV DN 80 | PCV-501/505/509/513 | 4 | 1 | Pneumatic explosion-proof control ball valve | Pg10kg/cm2; medium: nitrogen,T＜100℃,DC24V,explosion-proof Model:- VQ6T47H-10C, DN 80,Size:-163mm Make:- Gonkai | 0 | 0
[6 empty] | FSV-506 PNEUMATIC BUTTERFLY VALVE - DN250 | 1
[6 empty] | FSV502/511 PNEUMATIC BALL VALVE -DN25 | 5
[6 empty] | FSV-512 PNEUMATIC 3 WAY BALL VALVE -DN25 | 3
[6 empty] | FSV-507/508 PNEUMATIC BALL VALVE -DN40 | 6
[6 empty] | FSV401/402PNEUMATIC BALL VALVE -DN50 | 2
[6 empty] | FSV-509/535PNEUMATIC BALL VALVE -DN50 | 2
[6 empty] | FCV-502PNEUMATIC BALL VALVE -DN40 | 1
[6 empty] | FCV-501 PNEUMATIC BALL VALVE -DN80 | 1

## SOV
SNO | SHORT DESCRIPTION | Qty Instld | Qty Req | Item | Specification | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_BOKE 4M310-08 | 39 | 10 | solenoid valve | Make - BOKE, Model no-4M310-08, Pressure-0.15-0.8MPa | 10 | 1
2 | PCI_BOKE 4V310-10 | 9 | 3 | solenoid valve | Make - BOKE, Model no-4V310-10, Pressure-0.15-0.8MPa | 8 | 8
3 | PCI_ZMF-Y-76S | 40 | 10 | Solenoid Pulse valve for Bag Filter | Model no-ZMF-Y-76S, Supply Voltage:- 24 VDC | 4 | 3
4 | PCI_LIFT VALVE | 8 | 2 | LIFT Valve for Bag filter | Model- 4v310-10 , Pressure- 1.5-8 kgf/cm2, Make- KUROGANE | 0 | 0
SNO | SHORT DESCRIPTION | Qty Instld | Qty Req | Item | Specification | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_POSTNR_YT1000RDi131 | 8 | 2 |  | Make- YTC, Model no-YT1000RDi131, Serial No-17654, Explosion Proof:Exiall CT6, Input Signle-4῀20mADC, Ambient temp- -20῀70⁰C, Supply pressure- 1.4῀7.0 kgf/cm2 | 0 | 0
2 | PCI_POSITNR_YT1000LS1 | 12 | 3 |  | Make- YTC, Model no-YT1000LS1, Serial No-13118410, Explosion Proof:Exiall CT6, Input Signal-4 to 20mADC, Ambient temp-20 to 60⁰C, Supply pressure- 1.4 to 7.0 kgf/cm2 | 0 | 0

## POS'R
SNO | SHORT DESCRIPTION | Qty Instld | Qty Req | Item | Specification | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC
1 | PCI_POSTNR_YT1000RDi131 | 8 | 2 |  | Make- YTC, Model no-YT1000RDi131, Serial No-17654, Explosion Proof:Exiall CT6, Input Signle-4῀20mADC, Ambient temp- -20῀70⁰C, Supply pressure- 1.4῀7.0 kgf/cm2 | 0
2 | PCI_POSITNR_YT1000LS1 | 12 | 3 |  | Make- YTC, Model no-YT1000LS1, Serial No-13118410, Explosion Proof:Exiall CT6, Input Signal-4 to 20mADC, Ambient temp-20 to 60⁰C, Supply pressure- 1.4 to 7.0 kgf/cm2 | 0

## LOAD CELL
SL.NO | SHORT DESCRIPTION | Qty Instld | Qty Req | TAG NO | DESCRIPTION | INSTALATION SITE | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_LOAD CELL-RTD 4.7T | 12 | 3 | WT-501,WT-502,WT-503,WT-504 | SCHENCK PROCESS Load Cell Type-RTD 4.7T Accuracy (+/-)0.02% with zero balance Input Resistance 4480 ohms (+/-50 ohms) Output Resistance 4010 ohms (+/-50 ohms) Loadcell Sensitivity 2.85mV/V Loadcell Excitation Voltage 12 V AC | INJECTION VESSEL | 2 | 2
2 | PCI_LOAD CELL-RTD 68T | 7 | 2 | WT-301,WT-303 | SCHENCK PROCESS Load Cell Type-RTD 68T Input Resistance 4480 ohms (+/-50 ohms) Output Resistance 4010 ohms (+/-50 ohms) Loadcell Sensitivity 2.85mV/V Loadcell Excitation Voltage 12 V AC Accuracy (+/-)0.02% with zero balance | PCS &FCS | 0 | 0
3 | PCI_LOAD CELL-PWS 100KG | 2 | 1 | WT-302 | SCHENCK PROCESS Platform Load Cell, Type-PWS 100 kg Accuracy (+/-) 0.05% Input Resistance 390 ±10 Ω Output Resistance 350 ±2 Ω Loadcell Sensitivity 2 ±0.002 mV/V Loadcell Excitation Voltage 6 V AC | WEIGH FEEDER | 0 | 0
4 | PCI_ENCODER | 1 | 1 | NA | SPEED SENSOR TYPE - Type-FGA 1O IP-67 EXC VOL-(5-25V) Cable Length (m)-5mtr |  | 0 | 0
5 | PCI_JAM SWITCH | 22 | 6 | FS-515 TO FS 536 | MAKE- SWR FLOW JAM SWITCH, MAKE- SWR POWER SUPPLY-18 -24V DC/AC, RANGE (0-2M) MODEL :89/336/EEC | MBF1&2 | 0 | 0
6 | PCI_COAL FLOW METER | 2 | 1 | FT-514&FT-513 | Provided by power supply/conditioning PCBSFI 15-30VDC, 100mA max.Conduit Connection: (2) 1/2" NPT Detection Range: 0 to 10’ free air Sensitivity: Switch selectable HI/LOW Minimum Velocity: 2.5 ft/sec (762 mm/sec) Output:4-20mA Process Connection 1-1/4" NPT &DN50 Flange(Seals Adapter) Pipe diameterΦ63.5×7 | COAL CONVEYING LINE | 0 | 0
| DISOMAT TERSUS CONTROLLER | 6 | 2 |  |  |  | 1 | 1
| SHENCKPROCESS WEIGHFEEDER | 1 | 1 |  |  |  | 1 | 1

## Analyser
SL.NO | SHORT DESCRIPTION | Qty Instld | Qty Req | TAG NO | DESCRIPTION | INSTALATION SITE | Qty avbl | JUL | AUG | SEP | OCT | NOV | DEC | Spare to be indent
1 | PCI_ANALYSER_SV_1/4 | 8(2x4) | 2 |  | SOLENOID VALVE, 2 WAY MOC: SS Size: 1/4” Power Supply: 220VAC, 50 Hz, Make-ASCO Cat No- SCX5202C220V | SOV-104,106 | 0 | 0
2 | PCI_ANALYSER_SV_1/2 | 24(6x4) | 6 |  | SOLENOID VALVE, 2 WAY MOC: BRASS Size: 1/2” Power Supply: 220VAC, 50 Hz SCX8210C094MB | SV101/102/ 103/105/10 6/107 | 6 | 5
3 | PCI_ANALYSER_GASCOOLER | 4(4x1) | 1 |  | SAMPLE GAS COOLER Dual Gas Path SS coils Power Supply: 220VAC, 50Hz,Mains- 230V AC 50 HZ Model No- C.G.EK. - 5 Gas charge- 134-A Super Refrigeration Industries. Com No-B042069B Including Temperature sensor | GC01, abb approved | 0 | 1
4 | PCI_ANALYSER_PERISTALTIC_PUMP | 8(4x2) | 2 |  | PERISTALTIC PUMP Power Supply: 220VAC, 50 Hz,Make- ASF Thomas POWER-5.5w S3;40 DEG- 2 MIN ON/2 MIN OFF REF S. NnO.-70300001 | PP01 | 2 | 4
5 | PCI_BV_1/4 | 12(4x3) | 3 |  | 2 Way Ball Valve, SS316, 1/4 ”- Make- Baldota. | BV01,BV02,BV04 | 0 | 0
6 | PCI_SV_3WAY_1/4 | 8(4x2) |  |  | SOLENOID VALVE, 3 WAY MOC: SS Size: 1/4” Power Supply: 220VAC, 50 Hz, Make- ASCO CAT NO- SCX8320A201V | SV01/SV02 | 0 | 0
7 | PCI_BV_5WAY_1/4 | 4(1x4) |  |  | 5 Way Ball Valve, SS316, ¼ ", ABB Vendor approved- | BV03 | 0 | 0
8 | PCI_ANALYZER_PUMP | 8(4x2) | 2 |  | SAMPLE & BYPASS PUMP Capacity: 280 LPH Power Supply: 220VAC, 50 Hz, Make- knf Type- PM31272-86 Power- 55W,I-0.6A. | MP01, MP02 | 2 | 2
9 | PCI_GAS_FLOW_METER | 4(4x1) | 1 |  | GLASS TUBE FLOWMETER WITH P&F MAKE RING SENSOR UNIT Range: 7-70 LPH Size: ¼”, Make- PLACKA Model no- GA- 10 | FM01 | 0
[7 empty] | 0 | 0
10 | PCI_ANALYZER_SWITCHAMPLIFIER | 4(4x1) | 1 |  | SWITCHING AMPLIFIER (For low Flow Alarm) Power Supply: 24VDC | SA01 | 0 | 0
11 | PCI_ANALYZER_COND_MONITOR | 4(4x1) | 1 |  | CONDENSATE MONITOR with membrane Filter papers, ABB Vendor approved | CM01 | 0 | 0
12 | PCI_ANALZER_SU | 4(4x1) | 1 |  | SWITCHING UNIT (For Condensate alarm) Power Supply: 220VAC, 50 Hz E.L.B. ER 144/A Make- ABB | SU01 | 0 | 0
13 | PCI_ANALZER_PLC | 4(4x1) | 1 Set |  | PLC (AC500 SERIES) With CPU(PM-554-R) And Necessary I/O Cards(DO-571) Power Supply: 24VDC PL01- CPU PM554-RP-AC 8DI 24VDC 6DO-R 240VAC 2A -01 No. Module- DO 571-8DO-R 240VAC 2A- 1No. DO 571 8DO-R 240VAC 2A- 1No. Make- ABB | PL01 | 0 | 1
14 | PCI_ANALYSER_HMI\ | 4(4x1) | 1 |  | HMI DISPLAY, 4.3” Power Supply: 24VDC With PLC interconnecting cable Part no- 1sAP504100R0001 24V- 0.25A Class 2 V-100701A07006140 Ref S no- AA4001005000022478AA Make- ABB | HD01 | 0 | 0
15 | PCI_ANALSZER_CONTROLLER\ | 4(4x1) | 1 |  | EASYLINE ANALYZER (EL3000 series) Power Supply: 220 VAC, 50Hz Output: 4 - 20 mA, Per Component With DI/DO card With 19” Rack Mounted Housing Enclosure: IP20. With Uras 26 Module Measuring Component 1: CO Measuring Range 1: 0 To 2 Vol% With Magnos 28 Module Measuring Component 1: O2 Measuring Range 1: 0 To 21 Vol% MAke- ABB | GA01 | 1 | 0
16 | PCI_ANALYZER_PROXY_DETECTOR | 4 | 1 |  | MTL5516C SWITCH/ PROXIMITY DETECTOR INTERFACE 2-channel, with line fault detection Response time: 10ms maximum 10ms maximum Contact rating (Safe Area): 10W, 0.5A, 35V dc 250V ac, 2A, cosØ >0.7, 40V dc, 2A, resistive load Contact rating (Zone 2): 10W, 0.5A, 35V dc 35V, 2A, 100VA. MAke-Eaton Electric Limited, |  | 0 | 0
17 | PCI_ALALYZER_TIC | 8(4x2) | 2 |  | Dixell XR03CX XR03CX- 5Noco LIFDBXB5AA T-60 Deg C R.H.-20-85 % Probe- 3.5 VA Max- NTC |  | 0 | 0
18 | ceramic filter | 8 | 4 |  | ceramic filter |  | 4 | 4
19 | probe o ring | 8 | 10 |  | probe o ring |  | 0 | 2
20 | probe filter | 4 | 50 |  | probe filter |  | 0 | 0
21 | GLASSWOOL FILTER | 8 | 8 |  |  |  | 2 | 2

## Sheet1
SPARES IN PCI PLANT
SL no | Description | Qty | Location | JUL | AUG | SEP | OCT | NOV | DEC
1 | THERMOCOUPLE | 1 | RACK-1 ANALYSER ROOM
2 | RTD | 6
3 | CAT6 CABLE | 2 BOX
4 | LPBS JB | 1
5 | BAGFILTER DIAPHGRAM SOV | 4
6 | HOOTER WITH RED LIGHT | 2
7 | MICROWAVE SOLIDS FLOW MONITORS | 2
8 | CHINESSE SMALL -JB | 4
9 | CHINESSE BIG- JB | 2
10 | 8MM BALL VALVE | 13
11 | 3 WAY MANIFOLD | 19
12 | 1/2" BALL VALVE | 1
SL no | Description | Qty | Location
1 | DOME VALVE ACTUATOR | 1 | RACK- 2 ANALYSER ROOM
2 | PULLCORD SWITCH FOR CONVEYOR | 2
3 | BELTSWAY SWITCH FOR CONVEYOR | 2
4 | CO TRANSMITTER | 2
5 | O2 TRANSMITTER | 1
6 | PATCH KIT | 1 BOX
7 | NOTIFIER (FDA SYSTEM) | 2
8 | NOTIFIER CONTROL UNIT (FDA SYSTEM) | 7
9 | SMALL JB (FDA SYSTEM) | 2
10 | FIRE DETECTOR (FDA SYSTEM) | 15
11 | MICROWAVE SOLIDS FLOW MONITORS | 2
12 | ALARM INDICATORS (FDA SYSTEM) | 4
13 | CONTROL CARD (FDA SYSTEM) | 1
14 | CONTROL DISPLAY UNIT (FDA SYSTEM) | 1
15 | CONTROL POWER SUPPLY UNIT (FDA SYSTEM) | 1
16 | ABB CONTROLLER PCB DEFECTIVE | 1
17 | PERISTALIC PUMP | 5
18 | BLANK MODULE PLATES | 2
19 | SMALL FIBER JBS | 6
20 | T-TYPE GI CONNECTOR | 47
21 | T JOINT WELDEBLE | 48
22 | 1/2" GI NIPPLE | 33
23 | STRAIGHT CONNECTOR | 37
24 | 8MM-10MM BALL WALVE | 30
25 | 1/2" SS SOCKET | 1
26 | 1/2"WELDABLE UNION | 45
27 | LIMIT SWITCH BOLTS&NUTS | 100
28 | U TYPE 2" | 50
29 | SCHENCK PROCESS DEFECTIVE CONTROLLER | 1
30 | PULL CORD ROPE | 50MTR
31 | PROFIBUS CABLE | 150MTR
SL no | Description | Qty | Location
1 | 1/4 NIPPLE | 16 | RACK-3 ANALYSER ROOM
2 | BENT IRON JOINT | 50
3 | 1/4 T-TYPE CONNECTOR | 10
4 | 1/2" WELDABLE SOCKET | 40
5 | 1/2" -3/4 STRAIGHT CONNECTOR | 47
6 | 1/4THREADED SOCKET SS | 15
7 | U TYPE 1/2" | 20
SL no | Description | Qty | Location
1 | PRESSURE TRANSMITTER DIAPHRAGM TYPE | 1 | CABINET-1 PLC ROOM
2 | PRESSURE TRANSMITTER (0-1 KG/CM2) | 1
3 | PRESSURE TRANSMITTER (0-10 KG/CM2) | 1
4 | PRESSURE TRANSMITTER (0-0.2 KG/CM2) | 1
| PRESSURE TRANSDUCER 0-25 BAR | 1
5 | VIBRATION TRANSMITTER | 6
6 | PVC TUBE 8MM | 1BOX
7 | PVC TUBE 10MM | 1BOX
8 | PRESSURE GAUGE (0-1 MPA) | 1
9 | PRESSURE GAUGE (0-16 KG) | 1
10 | PRESSURE GAUGE (0-1 KG) | 1
11 | PRESSURE GAUGE (0-10KG) SMALL | 3
12 | TEMPERATURE GAUGE (0-100 deg C) | 1
13 | TEMPERATURE GAUGE (0-180 deg C) | 1
14 | RADAR TYPE LEVEL TRANSMITTER (0-5 MTR) | 1
15 | LOADCELL 4.7 TON | 3
16 | RTD &TC TRANSMITTER | 5
18 | RTD SENSOR (COMPRESSOR ITEMS) | 2
19 | THERMISTOR(COMPRESSOR ITEMS) | 2
20 | SOV 110V(COMPRESSOR ITEMS) | 6
21 | PRESSURE TRANSDUCER 225 PSI (COMPRESSOR ITEMS) | 3
22 | PRESSURE TRANSDUCER 100 PSI (COMPRESSOR ITEMS) | 2
23 | VACCUM TRANSDUCER 0-15 PSI (COMPRESSOR ITEMS) | 1
24 | CHECK VALVE KIT (COMPRESSOR ITEMS) | 2
25 | FLAME DETECTOR | 1
26 | FLOW TRANSMITTER (0-100MPA) | 1
27 | FLOW JAM SWITCH | 1
28 | PRESSURE TRANMITTER (0-10KG) | 1
29 | ZERO SPEED SWITCH(ZSS 110V AC) | 3
SL no | Description | Qty | Location
1 | SCHENCK PROCESS DISO BOX | 2 | CABINET-2PLC ROOM
2 | LIU UNIT | 4
3 | D-LINK ADAPTER PANNEL | 1
4 | D-LINK PATCH CORD | 1 BOX
5 | CAMERA CABLE | 50MTR
6 | RTD CABLE FOR VRM ROLLER BEARING TEMP | 40 MTR
7 | 2 PAIR TELEPHONE CABLE | 3 ROLL
12 | HYDRAULIC SOLENOID VALVE SET | 1 SET
SL no | Description | Qty | Location
1 | 8 MM PUSH FIT STRAIGHT CONNECTOR | 29 | CABINET-3 PLC ROOM
2 | 10 MM PUSH FIT STRAIGHT CONNECTOR | 14
3 | 10 MM 3/4 CONNECTOR | 19
4 | 8 MM 3/4 CONNECTOR | 20
5 | 10 MM T-TYPE PUSH FIT CONNECTOR | 16
6 | 8 MM T-TYPE PUSH FIT CONNECTOR | 15
7 | 1/2 " TO 1/4 BRASS FITTINGS | 6
8 | 10 MM PUSH FIT 1/2" CONNECTOR | 11
9 | O RING FOR MANIFOLD | 25
10 | 8 MM PUSH FIT 1/4 CONNECTOR | 35
11 | 10 MM PUSH FIT 1/4 CONNECTOR | 43
12 | SIEMENS 24VDC PSU | 1
13 | SIEMENS BUS CONNECTOR | 7
14 | AUMA 24VDC PSU | 1
15 | 220 VAC RELAY | 4
16 | PLC -CPU CONNECTOR FOR PC | 2
17 | 220VAC G-50 COIL | 2
18 | VGA CABLE | 1
19 | MS OFFICE SOFTWARE CD | 1
20 | ABB GAS ANALYZER SOFTWARE CD | 2
21 | D-LINK PATCH CORD DUPLEX | 2
22 | RS485-RS232 CONVERTER WITH CONNECTER | 1
23 | ALL IN ONE CARD READER | 2
24 | AC REMOTE | 3
25 | 24VDC SOV FOR LPG LINE IN HGG | 1
26 | DISOMAT SOFTWARE CD | 5
27 | ANCHOR SPIKE GUARD | 1
28 | SCHENCK PROCESS WEIGH FEEDER ELECTRONIC CARD | 1
29 | UPS KEY | 2
30 | PA SYSTEM TABLE TOP | 1
31 | HART | 1
32 | MASIBUS SOURCE (ma & mv) | 1
33 | MANNUALS & DRAWINGS
34 | MANNUALS & DRAWINGS
SL no | Description | Qty | Location
1 | FSV-506 PNEUMATIC BUTTERFLY VALVE - DN250 | 1 | IN STORE
2 | FSV502/511 PNEUMATIC BALL VALVE -DN25 | 5 | ANALYSER ROOM
3 | FSV-512 PNEUMATIC 3 WAY BALL VALVE -DN25 | 3
4 | FSV-507/508 PNEUMATIC BALL VALVE -DN40 | 6
5 | FSV401/402PNEUMATIC BALL VALVE -DN500 | 3
6 | FSV-509/535PNEUMATIC BALL VALVE -DN50 | 2
7 | FCV-502PNEUMATIC BALL VALVE -DN40 | 1
8 | FCV-501 PNEUMATIC BALL VALVE -DN80 | 1

## AIR COMPRESSOR
AIR COMPRESSOR SPARES
SNO | SHORT DESCRIPTION | TAG | Qty Instld | Qty Req | Item | Specification | Qty | JUL | AUG | SEP | OCT | NOV | DEC
1 | SOLENOID VALVE FOR LOAD | 1SV | 2 | 1 | SOV
2 | DISCHARGE CONDENSATE VALVE | 6SV | 2 | 1 | SOV
3 | DISCHARGE CONDENSATE VALVE | 9SV | 2 | 1 | SOV
4 | PRESSURE TRANSDUCER FOR INLET VACCUM | 1AVPT | 2 | 1 | PT
5 | 2ND STAGE INLET PRESSURE | 2APT | 2 | 1 | PT
6 | 2ND STAGE DISCHARGE PRESSURE | 3APT | 2 | 1 | PT
7 | PACKAGE DISCHARGE PRESSURE | 4APT | 2 | 1 | PT
8 | OIL FILTER INLET PRESSURE | 5OPT | 2 | 1 | PT
9 | BEARING OIL PRESSURE | 6OPT | 2 | 1 | PT
10 | 1ST STAGE DISCHARGE TEMPERATURE | 2ATT | 2 | 1 | TT
11 | 2ND STAGE INLET TEMPERATURE | 3ATT | 2 | 1 | TT
12 | 2ND STAGE DISCHARGE TEMPERATURE | 4ATT | 2 | 1 | TT
13 | BEARING OIL TEMPERATURE | 5OTT | 2 | 1 | TT
14 | PACKAGE DISCHARGE TEMPERATURE | 7ATT | 2 | 1 | TT
15 | AIR DRYER TEMP PROBE -1 | PB1 | 2 | 1 | THERMOSTAT
16 | AIR DRYER TEMP PROBE -2 | PB2 | 2 | 1 | THERMOSTAT
17 | AIR DRYER TEMP PROBE -3 | PB3 | 2 | 1 | THERMOSTAT
18 | AIR DRYER TEMP PROBE -4 | PB4 | 2 | 1 | THERMOSTAT
19 | FAN PRESSURE SWITCH | FPS | 2 | 1 | PS
20 | COMPRESSOR THERMAL SWITCH | CTS | 2 | 1 | TS
21
22

## Sheet2
Spare AO | Spare AO | XC410 | 13,14 | PQW264 | C2 | AO | 4-20 ma o/p
Spare AI | Spare AI | XE307 | 26+,27- | PIW 554 | C3 | AI (4-20mA) | 4W
Spare AI | Spare AI | XE307 | 31+,32- | PIW 556 | C3 | AI (4-20mA) | 4W
Spare DO_Q 26.0 | Spare DO | XE203 | 41,51 | Q 26.0 | C3
Spare DO_Q 26.1 | Spare DO | XE203 | 42,52 | Q 26.1 | C3
Spare DO_Q 26.2 | Spare DO | XE203 | 43,53 | Q 26.2 | C3
Spare DI |  | XF101 | 62,72 | I 51.1 | C3
Spare DI |  | XF101 | 63,73 | I 51.2 | C3
Spare DI |  | XF101 | 64,74 | I 51.3 | C3
Spare DI |  | XF101 | 65,75 | I 51.4 | C3
Spare DI |  | XF101 | 66,76 | I 51.5 | C3
Spare DI |  | XF101 | 67,77 | I 51.6 | C3
Spare DI |  | XF101 | 68,78 | I 51.7 | C3